## Docs for Neptune
Constanat Documents & there Status for Neptune
Sr. No | Document Name | Status
1 | C902 | Available
2 | A210GRID | Available
3 | A210PC | Available
4 | A210ACE | Available
5 | A210CGE | Available
6 | A210CBM | Available

## Calculated Constants
Sr. No | Title | Sub - Title | Input Name | Input Value - Default | Input Value | Units | Note in Tool | Reffrred | Status
1 | Project Data | Design Parameters | Frame Size | 7HA.03 FL22 | 7HA.03 FL22 |  | as per GT Attribute
1 | Project Data | Design Parameters | Fuel Type | Gas_Only | Dual_Fuel |  | as per GT Attribute
1 | Project Data | Design Parameters | Shaft Type | Multi | Multi |  | as per GT Attribute
1 | Project Data | Design Parameters | Droop Regulation | 4 | 4 | % | A210GRID (KDROOP_STD) | A210GRID (KDROOP_STD)
1 | Project Data | Design Parameters | Guaranteed Baseload MW Output | 354 | 337.902 | MW | Enter from A210PC> Deltas-Live tabs Base Loads Design Temp> Output converting to MW | .
1 | Project Data | Design Parameters | Island Target Load | 15 | 15 |  | Get the estimated island load setting from customer. If the setting varies > 10-20MWATTthen an analog input from the customer/DCS is needed in place of the constant. | .
1 | Project Data | Design Parameters | HDAS | None | CW_FDWTR |  | as per GT Attribute
1 | Project Data
1 | Project Data | Ambient Conditions | Site Ambient Pressure | 14.69 | 13.6335 | psia | Enter from A210PC> Deltas-Live tab> Base Load> Design Temps Ambient Pressure - psia
1 | Project Data | Ambient Conditions | Site Ambient Temperature | 89 | 104 | degF | Enter from A21OPC> Deltas-Live tab> Base Load> Design Temp> Ambient Temperature - F
1 | Project Data
1 | Project Data | Generator Inputs | Generator Rating (MVA) | 493 | 525 | MVA | See C902> Generator Rating section > Apparent Power | C902 (Generator Data)
1 | Project Data | Generator Inputs | Line Voltage | 25 | 24 | KV | See 0444> PT Upstream of line breaker (if exists) or if not than the Generator Breaker | C902 (Generator Data)
1 | Project Data | Generator Inputs | BusXformer Low side voltage | 15.75 | 24 | KV | See 0444> BusXformer Low side volt from customer bus low side (Usually = Gen. voltage depending on placement of Step-up Xformer on One-Line Diagram) | On One Line Diagram (0444)
1 | Project Data | Generator Inputs | Frequency | 60 | 60 | HZ | See C902> Generator Rating sections Electrical Frequency | C902 / (0444)
1 | Project Data | Generator Inputs | Generator Rating (MW) | 394.4 | 446.3 | MW | See C902> Generator Rating section> Active Power | C902 / (0444)
1 | Project Data | Generator Inputs | Generator Gas Pressure (Hydrogen) | 60 | 75 | psig | See C902> Generator Rating sections Gas Pressure
1 | Project Data | Generator Inputs | Is Second Breaker_Synch attribute within the GT controller set to Serial? | yes | yes |  | See G* > Attributes if Serial is selected
1 | Project Data | Generator Inputs | Does AOI 6 GPP Elementary Drawing show that the 52L trip circuit between the TCP and GPP exists? | yes | Yes |  | See A016 GPP Elem> Page Description: 52L Trip Circuit | page no : 64
1 | Project Data
1 | Project Data | Generator Capability | PF from Generator Capability Curve | 0.85 | 0.85 |  | Generator rated PF. Can be found in the C902 Reactive Capability Curve Sheet | Enter Generated PF
1 | Project Data | Generator Capability | DKVCMX - Max MVAR from Generator Capability Curve | 235 | 280 | MVARS | Max MVAR value corresponding on the Y-Axis of the intersection point of power factor line and capability curve | Ref C902 Generator Capability Curve
1 | Project Data | Generator Capability | DKVCMN - Min MVAR from Generator Capability Curve | -140 | -200 | MVARS | Min MVAR value corresponding on the Y-Axis of the intersection point of power factor line and capability curve | Ref C902 Generator Capability Curve
2 | Exhaust Purge | Exhaust Purge Calculation | High Exhaust Pressure Alarm Level | 23.4 | 18.09 | in H2O | A210ACE or A010ACE (K63EAH) | A210ACE (Default in Library)
2 | Exhaust Purge | Exhaust Purge Calculation | High High Exhaust Pressure Trip Level | 26.33 | 20.5 | in H2O | A210ACE or A010ACE (K63EAHH) | A210ACE (Default in Library)
2 | Exhaust Purge | Exhaust Purge Calculation | Exhaust Damper | No | No |  | as per GT Attribute | Should match the Attribute
2 | Exhaust Purge
2 | Exhaust Purge | Exhaust Program Inputs | Exhaust Temp Control Curve TX Ref Isotherm | 1275 | 1275 | degF | Enter from A210PC> MBC Converter Tab | Should match TTK I
3 | Gas Fuel | Gas Operating Conditions | Gas-Base Load Nominal Fuel flow | 33.05 | 42.8399 | lb/sec | A010PC (-> Deltas-> Live tab->Base Load-> Design Temp-> Fuel Flow) | A210PC (Delta ->)
3 | Gas Fuel | Gas Operating Conditions | Gas-FSNL Nominal Fuel Flow | 5.91 | 8.4428 | lb/sec | A010PC (-> Deltas-> Live tab-> FSNL, Min IGV -> Fuel Flow) | A210PC (Delta ->)
3 | Gas Fuel | Gas Operating Conditions | Gas Fuel Pressure - Min | 517 | 535 | psig | See A210CGE> Min Operating Pressure at FGI | A210CGE (Inputs-> )
3 | Gas Fuel | Gas Operating Conditions | Gas Fuel Pressure - Max | 652 | 650 | psig | See A210CGE> Max Operating Pressure at FGI | A210CGE (Inputs-> )
3 | Gas Fuel | Gas Operating Conditions | Gas Fuel Temp - Target Temp | 410 | 440 | degF | See A210CGE> Target temperature for baseload operation
3 | Gas Fuel | Gas Operating Conditions | Gas Fuel Temp - Maximum Allowable/Design Temp | 465 | 465 | degF | See A210CGE> Gas Fuel Temp — Maximum Allowable/Design Temp. If input does not exist contact A210CGE owner for correct value. | Value needs to be greater than Target temperature for baseload operation if it is not contact A210CGE owner | .
3 | Gas Fuel | Gas Operating Conditions | Gas Fuel Temperature - Min | 80 | 63 | degF | See A210CGE> Hydrocarbon or Moisture Dewpoint + Superheat | A210CGE (Inputs->
3 | Gas Fuel
3 | Gas Fuel | Gas Program Inputs | Fuel gas temperature hydrocarbon dew point low limit | 100 | 63 | degF | See A210CGE> Hydrocarbon Dewpoint + Superheat
3 | Gas Fuel | Gas Program Inputs | Gas fuel temperature moisture dew point low limit | 40 | 63 | degF | See A210CGE> Moisture Dewpoint + Superheat
3 | Gas Fuel | Gas Program Inputs | Gas fuel pressure high high limit | 670 | 725 | psig | See A210CGE> Max allowable pressure
3 | Gas Fuel | Gas Program Inputs | Gas Valve Cg Value | PCHE | PCHE |  | Should be based on Max temp for MWI Compliance | as per GT Attribute
3 | Gas Fuel
3 | Gas Fuel | Gas Fuel Properties | O2 - Oxygen - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | N2 - Nitrogen - Gas | 0.296 | 0.064 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | CO - Carbon Oxide - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | CO2 - Carbon Dioxide - Gas | 0.156 | 0.025 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | H2O - Water Vapour - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | Ar - Argon - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | H2 - Hydrogen - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | CH4 - Methane - Gas | 94.727 | 0.83 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C2H6 - Ethane - Gas | 4.569 | 0.066 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C3H8 - Propane - Gas | 0.212 | 0.0007 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C4H10 - N-Butane - Gas | 0.032 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C4H10 - iso-Butane - Gas | 0 | 0.005 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C5H12 - N-Pentane - Gas | 0.007 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C5H12 - I-Pentane - Gas | 0 | 0.005 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C5H12 - neo-Pentane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C6H14 - Hexane - Gas | 0.001 | 0.005 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C7H16 - n-Heptane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C8H18 - N-Octane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C9H20 - n-Nonane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C10H22 - n-Decane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C11H24 - n-Undecane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C12H26 - dodecane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C13H28 - n-tridecane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | C14H30 - n-tetradecane - Gas | 0 | 0 | pct |  | A210CGE
3 | Gas Fuel | Gas Fuel Properties | SO2 - Sulfur Dioxide - Gas | 0 | 0 | pct |  | A210CGE
4 | LIQUID FUEL | Liquid Fuel Properties | Liquid Fuel Specific Gravity | 93 | 93 | 60/60F | Liquid Fuel constants are under development
4 | LIQUID FUEL | Liquid Fuel Properties | Liquid Fuel LHV | 94 | 94 | BTU/lb | Liquid Fuel constants are under development
4 | LIQUID FUEL | Liquid Fuel Properties | 951-4-21 20rr,A setting - Lubricity Additive Flow (CC/MIN) | 95 | 95 |  | Liquid Fuel constants are under development
4 | LIQUID FUEL | Liquid Fuel Properties | FQKLMMN | 96 | 96 | lb/sec | Liquid Fuel constants are under development
4 | LIQUID FUEL | Liquid Fuel Properties | Base load liquid fuel flow (Design temp) • FQKLW | 49.66 | 42.8924 | lb/sec | Obtain from AOIOPC> Deltas_Lives> OTR> Design Temp> Fuel Flow where Water/ Fuel Ration have values vs zeros
4 | LIQUID FUEL
4 | LIQUID FUEL | Liquid Heat Consumption |  | 97 | 97 |  | Liquid Fuel constants are under development
5 | Device Summary | Device Setting | Gen Gas Pressure Nominal PT-2950 | 75 | 75 | psig | Ref C902 to get Gen Press from the Generator Rating Section in psig
5 | Device Summary | Device Setting | Cooling Water VTR7-1 Setting | 66 | 66 |  | Obtain from Device Summary Check for settings in MLI 0453 system in Device Summary, If not found leave as it is. | Device Summary -> MLI 0453 N/A
5 | Device Summary | Device Setting | Cooling Water VTR7-1 Deadband | 67 | 67 |  | Obtain from Device Summary Check for settings in MLI 0453 system in Device Summary, If not found leave as it is. | Device Summary -> MLI 0453 N/A
5 | Device Summary | Device Setting | Cooling Water Flow Meter Setting-High Flow setpoint 96CW-I | 4510 | 4510 | gpm | Obtain from Device Summary Check for settings in MLI 0453 system in Device Summary, If not found leave as it is. | Device Summary -> MLI 0453 N/A
5 | Device Summary | Device Setting | Cooling Water Flow Meter Setting-High-High Flow setpoint 96CW-2 | 4636 | 4636 | gpm | Obtain from Device Summary Check for settings in MLI 0453 system in Device Summary, If not found leave as it is. | Device Summary -> MLI 0453 N/A
5 | Device Summary | Device Setting | Evap Cooler | Yes | Yes |  | Check Device Summary for 88AC | 88AC -1A,1B are available in 414load list
5 | Device Summary | Device Setting | Evap Cooler Input - KWLKACLL | 32.81 | 32.81 | % | Device Summary (96AC-21) | 96AC-21 is available in 414I report
5 | Device Summary | Device Setting | Evap Cooler Input - KWLKACL | 48.75 | 48.75 | % | Device Summary (96AC-21) | 96AC-21 is available in 414I report
5 | Device Summary | Device Setting | Evap Cooler Input - KWLKACH | 56.81 | 56.81 | % | Device Summary (96AC-21) | 96AC-21 is available in 414I report
5 | Device Summary | Device Setting | Evap Cooler Input - KWLKACHH | 72.81 | 72.81 | % | Device Summary (96AC-21) | 96AC-21 is available in 414I report
5 | Device Summary | Device Setting | Gas Startup Heater | None | None |  | Match attribute selection
5 | Device Summary | Device Setting | Gas Perform Heater | ShellandTube | None |  | Match attribute selection | as per PSR
5 | Device Summary | Device Setting | DWATT Low Value 96GG-1 | -449.9 | -50 |  | From the A016, set to 96GG-1 4mA value
5 | Device Summary | Device Setting | DWATT High Value 96GG-1 | 787.5 | 550 |  | From the A016, set to 96GG-1 20mA value
5 | Device Summary | Device Setting | 96QE-1 Lube Oil Pressure | Yes | Yes |  | see Device summary | Available in 414I
5 | Device Summary | Device Setting | 96QE-1A Lube Oil Current | Yes | No |  | see Device summary
5 | Device Summary | Device Setting | 72QEY-1 , 72QEY-2 Lube Oil step Relays | Yes | No |  | see Device summary
5 | Device Summary | Device Setting | 96ES-1 Seal Oil Pressure | Yes | Yes |  | see Device summary
5 | Device Summary | Device Setting | 96ES-1A Seal Oil Current | Yes | No |  | see Device summary
5 | Device Summary | Device Setting | 72ESY-1, 72ESY-2 Seal Oil step Relays | Yes | No |  | see Device summary
5 | Device Summary | Device Setting | Lube / Seal Oil Legacy | No | No |  | Set same as GT >Attribute Lube_Seal_Oil_Legacy | as per Issue 804612
5 | Device Summary | Device Setting